## Slide 2: Unit 4
10.4.25

## Slide 3: Programmable Logic Controller

## Slide 4: INPUT DEVICES:
Level SW
Flow SW
Thumbwheel SW
Limit Switch
Push Button

## Slide 5: OUTPUT DEVICES:
Motor | 
Solenoid | 
LED Display | 
Heater Coil | 
Lamp | 

## Slide 6: Typical PLC Input / Output (I/O) system connections

## Slide 7: RELAYS..

## Slide 8: Relay …….
A relay is an electro-mechanical operator switch.
It is a hardware switching device to control the electrical circuit by using switching logic.

## Slide 9
Relay
Simply: Relay has contacts and coil

## Slide 10
Two indicator lamps (RED and GREEN) are connected to a electromagnetic relay. A switch S1 is also connected to the coil terminal.
If S1 is closed GREEN bulb must glow, and when S1 is turned off RED bulb must glow. Develop relay logic diagram.

## Slide 11: Seal-in contact (Relay logic diagram)
M
          START STOP M

## Slide 12: Programming languages
The IEC 61131-3 standard specifies five distinct forms of programming languages for industrial controllers:
Ladder Diagram (LD)
Structured Text (ST)
Instruction List (IL)
Function Block Diagram (FBD)
Sequential Function Chart (SFC)
Not all programmable logic controllers support all 5 language types, but nearly all of them support Ladder Diagram (LD), which will be our primary focus….

## Slide 13: LADDER DIAGRAM
Programming languages for many industrial devices are limited by design.
One reason is simplicity: any programming language simple enough in structure for someone with no formal computer programming knowledge to understand is going to be limited in its capabilities.
Another reason for programming limitations is safety: the more flexible and unbounded a programming language is, the more potential there will be to unintentionally create complicated “run-time” errors when programming.

## Slide 14
SYMBOLS USED:
INPUT SYMBOLS:

## Slide 15: LADDER – related facts…

## Slide 16: dos and don'ts

## Slide 17: Example 1
A fan is to started and stopped from any one of the three locations.
Each location has a START & STOP button.
Soln:
The START switches as NO(NORMALLY OPEN) in parallel, &
The STOP switches as NC (NORMALLY CLOSED) in series….
START (3) switches STOP (3) SWITCHES FAN

## Slide 18: WITHOUT INTERLOCK
A motor can operate in two directions as per the operator selection.
The motor can rotate in the forward direction or in the reverse direction.
But the motor can rotate in only one direction at a time.
If we give both forward or reverse commands at the same time then the motor will be damaged.

## Slide 19: Interlocking.. concept
In general, the motor logics are equipped with many safety functions and other motor-related pushbuttons like start, stop, and emergency stop.
we can avoid these problems with help of an interlock program. This program is called Interlock with the first input priority.
…………TO insert the NC status of motor output commands in the input side to implement this interlock logic.
Insert NC status of the reverse command with forward selector switch, ……..IIILY NC status of forward command with the motor reverse selection switch

## Slide 20: Forward- Reverse operation of motor with interlock
PLC Interlock Video Tutorial in Insrumentationtools.com

## Slide 21: INTERLOCK further examples..
There are three machines, each with its own start-stop buttons. Only one may run at a time.
Construct a circuit with appropriate interlocking.

## Slide 23: INTERLOCK example
There are three machines, each with its own start-stop buttons. Any two/one may run at a time.
Reconstruct circuit with appropriate interlocking.

## Slide 25
THANK YOU…